| Cmt # | Dwg No. | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |
|  | Hall D Floor Plan/A103 | Abkemeier | Photon beam dump needs muon shielding of 10 meters total. This shielding should have a minimum radius of 1 meter centered on the beam line. Additionally need 3 meters of dirt surrounding the shielding to mitigate site boundary dose. Also requires 1 meter additional SEG block (steel) shielding for a length of 3 meters underneath the photon beam dump to prevent groundwater activation. Also needs 1 meter alcove in the center for containment of photon beam dump proper. |  |
|  | Hall D Foundation Plan/S105 | Abkemeier | Adjust labyrinth in Hall D collimator section to minimize “line of sight” neutrons for detector background, activation, and boundary dose. Have entrance start in opposite direction, and create labyrinth wall |  |
|  | Utility Plan/CU103A | Abkemeier | Need interlocked exclusion gate at the top of the Tagger Building truck ramp in order to establish an exclusion area to provide protection against a maximum credible accident scenario |  |
|  | Utility Plan Area B/CU103B | Abkemeier | Need interlocked exclusion gate at the top of the Hall D truck ramp in order to establish an exclusion area |  |
|  | Tagger Area Foundation Plan/S103 | Abkemeier | Need 2’ thick labyrinth wall for tagger building controlled access door to mitigate against maximum loss scenario |  |
|  | Tagger Area Plan and Tunnel extension/A102 | Abkemeier | Extend electron beam dump labyrinth walls to extend to maximum extent allowable in order to minimize neutron backscattering for detectors. Particularly, extend first wall to the corner where the electron beam dump area proper begins. Additionally, add 2 doors with 1” thick borated poly to minimize thermal neutron flux into detector region. One should be at the entry region, and one should be at the first SEG labyrinth wall. |  |
|  | Tagger Area Plan and Tunnel Extension/A102 | Abkemeier | Add 1 SEG block thickness (26” steel) around tagger building electron beam dump in all directions. This can be carved out from the 5’ thick concrete shielding walls. Change 2 labyrinth walls closest to the electron beam dump to 26” thick steel, instead of concrete blocks. Provide alcove for electron beam dump such that it is approximately 3 feet deep into surrounding steel shielding. |  |
|  | Hall D Foundation Plan/S105 | Abkemeier | Thicken controlled access labyrinth wall to 2’ thickness |  |
|  | Tagger Area Plan and Tunnel Extension/A102 | Abkemeier | Steel muon shielding should be 7 meters long with a radius of one meter surrounding the center of the beam line (i.e., 3 SEG block widths (13 inches across)) |  |
|  | Tagger Area Plan and Tunnel Extension/A102. | Abkemeier | Move truck ramp shielding block so that entrance passageway is between 2 parallel rows of shielding block |  |
|  | Tagger Area Foundation Plan/S103 | Abkemeier | Need concrete foundation to support 7 meters length of 2 meter diameter steel blocks |  |
|  | Hall D Foundation Plan/S105 | Abkemeier | Need concrete foundation to support 10 meters length of 2 meter diameter steel block |  |
|  | Hall D Floor Plan | Abkemeier | Move truck ramp shielding block so that entrance passageway is between 2 parallel rows of shielding block |  |
|  | Counting House Building Section/A303 | Abkemeier | Increase concrete thickness of foundation underneath and around collimator region in order to prevent groundwater activation. Thickness to be determined. |  |